Table 3: Structures in which Legionella was isolated and in which at least a second sampling operation was performed: summary of samplings’ results

| Structures analysed: type, ID | Sampling # | Declared disinfection treatment carried out before sampling | Sampling result (isolated Legionella, % positive samples) | Maximum Legionella load detected (UFC / L) |
| --- | --- | --- | --- | --- |
| Sports Centre, 3 | 1 | / | L. pneumophila sg1, 67% | 8x103 |
|  | 2 | Shock hyperchlorination |  | < 10 |
| Sports Centre, 6 | 1 | / | L. pneumophila sg2-14, 33% | 6x103 |
|  | 2 | Heat shock every day, showerhead management |  | < 10 |
| Sports Centre, 10 | 1 | / | L. pneumophila sg2-14, 100% | 1.2x104 |
|  | 2 | Shock hyperchlorination, heat shock and showerhead management |  | < 10 |
| Sports Centre, 11 | 1 | / | L. pneumophila sg1 and 2-14, 67% | 3x104 |
|  | 2 | Shock hyperchlorination and showerhead management | L. pneumophila sg1 and 2-14: 50%; L. pneumophila sg2-14: 25% | 1.4x105 |
|  | 3 | Shock hyperchlorination |  | < 10 |
| Sports Centre, 12 | 1 | / | L. pneumophila sg2-14, 100% | 6.2x104 |
|  | 2 | Shock hyperchlorination1 | L. pneumophila sg2-14, 75% | 5.7x104 |
|  | 3 | Shock hyperchlorination1 | L. pneumophila sg2-14, 83% | 3.0x104 |
| Sports Centre, 17 | 1 | / | L. pneumophila sg1, 25%; L. pneumophila sg 1 and 2-14, 25% | 1.6x104 |
|  | 2 | Shock hyperchlorination2 | L. pneumophila sg2, 67%; L. pneumophila sg 1 and 2-14, 17% | 3.2x104 |
|  | 3 | Shock hyperchlorination, heat shock every day, hydrogen peroxide | L. pneumophila sg1, 13% | 2x103 |
| Spa hotel, 36 | 1 | / | L. pneumophila sg1, 22.2%; L. pneumophila sg1 and spp., 11.1%; Legionella spp., 11.1% | 1.6x104 |
|  | 2 | Shock hyperchlorination every day |  | < 10 |
|  | 33 | / | Legionella spp., 18%; L pneumophila sg1: 10% | 4x103 |
|  | 43 | Shock hyperchlorination every day | Legionella spp.,71% L pneumophila sg1 e 2-14 and Legionella spp, 14% | 1x103 |
|  | 53 | Shock hyperchlorination every day | Legionella spp., 17% | 90 |
|  | 63 | Shock hyperchlorination every day | L. pneumophila sg2-14, 20%; Legionella spp., 20%; L. pneumophila sg1, 10% | 1.9x103 |
| Retirement home, 48 | 1 | / | L. pneumophila sg1, 100% | 850 |
|  | 2 | Shock hyperchlorination, heat shock every day | L. pneumophila sg1, 63% | 4.1x104 |
|  | 3 | Shock hyperchlorination, heat shock every day | L. pneumophila sg1, 25% | 150 |
|  | 4 | Shock hyperchlorination, heat shock every day | L. pneumophila sg1, 25% | 40 |
| Retirement home, 49 | 1 | / | L. pneumophila sg1, 100% | 750 |
|  | 2 | Shock hyperchlorination, heat shock every day | L. pneumophila sg1, 75% | 470 |
|  | 3 | Shock hyperchlorination, heat shock every day | L. pneumophila sg1, 50% | 10 |
|  | 4 | Shock hyperchlorination, heat shock every day |  | < 10 |

1 Carried out by the operator, not by a specialised technician

2 Performed only in sections of water systems leading to the distal points that were positive for Legionella

3 Taking into account the negativisation of the structure in the previous sampling operation, the third, fourth, fifth and sixth samplings were considered in the analyses as the first, second, third and fourth sampling operations, respectively.